## 设备配置
id | template | transport | rtu_device | rtu_baud | tcp_ip | tcp_port | slave | mysql_table | table_suffix | count_qt_addr | poll_ms | inter_frame_ms | timeout_ms | default_pt | default_ct | pt_ct_sync_enabled | pt_ct_sync_read_reg | pt_ct_sync_min_value | pt_ct_sync_max_value | comm_enabled | comm_probe_addr | comm_probe_count | comm_fail_threshold | comm_mysql_online_addr | comm_com_alarm_addr | comm_com_alarm_table
load_meter | amc_meter | rtu | /usr/dev/serial/com3 | 9600 |  |  | 1 | load_meter |  |  | 600 | 5 |  | 1 | 1 | TRUE | 3 | 1 | 30000 | TRUE | 3 | 1 | 3 | 0 | 3 | com_alarm
dg_meter | amc_meter | rtu | /usr/dev/serial/com3 | 9600 |  |  | 2 | dg_meter |  |  | 600 | 5 |  | 1 | 1 | TRUE | 3 | 1 | 30000 | TRUE | 3 | 1 | 3 | 0 | 4 | com_alarm
pv_meter | amc_meter | rtu | /usr/dev/serial/com4 | 9600 |  |  | 1 | pv_meter |  |  | 600 | 5 |  | 1 | 1 | TRUE | 3 | 1 | 30000 | TRUE | 3 | 1 | 3 | 0 | 5 | com_alarm
ess_meter | amc_meter | rtu | /usr/dev/serial/com4 | 9600 |  |  | 2 | ess_meter |  |  | 600 | 5 |  | 1 | 1 | TRUE | 3 | 1 | 30000 | TRUE | 3 | 1 | 3 | 0 | 6 | com_alarm
sun_pv | sun_pv | rtu | /usr/dev/serial/com1 | 9600 |  |  | 1 | sunpv | 1 | 617 | 600 | 10 | [7 empty] | TRUE | 4999 | 1 | 3 | 0 | 12 | com_alarm
agc | agc | rtu | /usr/dev/serial/com2 | 9600 |  |  | 1 | agc |  | 707 | 600 | 10 | [7 empty] | TRUE | 500 | 1 | 3 | 0 | 16 | com_alarm
pcs_smarten | pcs_smarten | tcp |  |  | 192.168.1.201 | 502 | 1 | pcs |  |  | 600 | 20 | [7 empty] | TRUE | 40164 | 1 | 3 | 0 | 2 | com_alarm
bamu_stack | bamu_stack | tcp |  |  | 192.168.1.210 | 502 | 1 | bamu |  | 708 | 600 | 20 | [7 empty] | TRUE | 1 | 1 | 3 | 0 | 1 | com_alarm
bamu_bms | bamu_bms | tcp |  |  | 192.168.1.210 | 502 | 1 | bms | 1 |  | 600 | 20 | [7 empty] | TRUE |  |  |  | 0 |  | com_alarm
bamu_air | bamu_air | tcp |  |  | 192.168.1.210 | 502 | 1 | air | 1 |  |  | 20 | [7 empty] | FALSE
dido | dido | tcp |  |  | 127.0.0.1 | 5020 | 1 | dodi |  |  | 500 | [8 empty] | TRUE | 100 | 1 | 3 | 0

## agc
name | type | fc | address | cluster_stride | bit | scale | bias | pt_exp | ct_exp
Online | virtual_comm
ABVoltage | u16 | 4 | 501
BCVoltage | u16 | 4 | 502
CAVoltage | u16 | 4 | 503
APhaseVoltage | u16 | 4 | 504
BPhaseVoltage | u16 | 4 | 505
CPhaseVoltage | u16 | 4 | 506
AFrequency | i16 | 4 | 507 |  |  | 0.01
BFrequency | i16 | 4 | 508 |  |  | 0.01
CFrequency | i16 | 4 | 509 |  |  | 0.01
APhaseCurrent | i16 | 4 | 513
BPhaseCurrent | i16 | 4 | 514
CPhaseCurrent | i16 | 4 | 515
APhaseActivePower | i16 | 4 | 516
BPhaseActivePower | i16 | 4 | 517
CPhaseActivePower | i16 | 4 | 518
TotalActivePower | i16 | 4 | 519
APhaseReactivePower | i16 | 4 | 520
BPhaseReactivePower | i16 | 4 | 521
CPhaseReactivePower | i16 | 4 | 522
TotalReactivePower | i16 | 4 | 523
APhaseApparentPower | i16 | 4 | 524
BPhaseApparentPower | i16 | 4 | 525
CPhaseApparentPower | i16 | 4 | 526
TotalApparentPower | i16 | 4 | 527
TotalActiveEnergy | u32_hi_lo | 4 | 536
TotalReactiveEnergy | u32_hi_lo | 4 | 528
TotalPowerFactor | i16 | 4 | 538 |  |  | 0.01
EngineOilLevel | i16 | 4 | 615 |  |  | 0.1

## amc_meter
name | type | fc | address | cluster_stride | bit | scale | bias | pt_exp | ct_exp
Online | virtual_comm
APhaseVoltage | u16 | 3 | 0x100 |  |  | 0.1 |  | 1
BPhaseVoltage | u16 | 3 | 0x101 |  |  | 0.1 |  | 1
CPhaseVoltage | u16 | 3 | 0x102 |  |  | 0.1 |  | 1
ABVoltage | u16 | 3 | 0x103 |  |  | 0.1 |  | 1
BCVoltage | u16 | 3 | 0x104 |  |  | 0.1 |  | 1
CAVoltage | u16 | 3 | 0x105 |  |  | 0.1 |  | 1
APhaseCurrent | i16 | 3 | 0x106 |  |  | 0.001 |  |  | 1
BPhaseCurrent | i16 | 3 | 0x107 |  |  | 0.001 |  |  | 1
CPhaseCurrent | i16 | 3 | 0x108 |  |  | 0.001 |  |  | 1
APhaseActivePower | i16 | 3 | 0x109 |  |  | 0.001 |  | 1 | 1
BPhaseActivePower | i16 | 3 | 0x10A |  |  | 0.001 |  | 1 | 1
CPhaseActivePower | i16 | 3 | 0x10B |  |  | 0.001 |  | 1 | 1
TotalActivePower | i16 | 3 | 0x10C |  |  | 0.001 |  | 1 | 1
APhaseReactivePower | i16 | 3 | 0x10D |  |  | 0.001 |  | 1 | 1
BPhaseReactivePower | i16 | 3 | 0x10E |  |  | 0.001 |  | 1 | 1
CPhaseReactivePower | i16 | 3 | 0x10F |  |  | 0.001 |  | 1 | 1
TotalReactivePower | i16 | 3 | 0x110 |  |  | 0.001 |  | 1 | 1
APhaseApparentPower | u16 | 3 | 0x115 |  |  | 0.001 |  | 1 | 1
BPhaseApparentPower | u16 | 3 | 0x116 |  |  | 0.001 |  | 1 | 1
CPhaseApparentPower | u16 | 3 | 0x117 |  |  | 0.001 |  | 1 | 1
TotalApparentPower | u16 | 3 | 0x118 |  |  | 0.001 |  | 1 | 1
APowerFactor | i16 | 3 | 0x111 |  |  | 0.001
BPowerFactor | i16 | 3 | 0x112 |  |  | 0.001
CPowerFactor | i16 | 3 | 0x113 |  |  | 0.001
TotalPowerFactor | i16 | 3 | 0x114 |  |  | 0.001
Frequency | u16 | 3 | 0x119 |  |  | 0.01
AbsorbActiveEnergyPrimary | u32_hi_lo | 3 | 0x3F |  |  | 0.001 |  | 1 | 1
ReleaseActiveEnergyPrimary | u32_hi_lo | 3 | 0x41 |  |  | 0.001 |  | 1 | 1

## bamu_air
name | type | fc | address | cluster_stride | bit | scale | bias | pt_exp | ct_exp
Online | bit | 2 | 0x8A5 | 200
OnOffStatus | u16 | 4 | 0xEAED | 100
OperationMode | u16 | 4 | 0xEAEE | 100
FanStatus | virtual
WaterPumpStatus | virtual
Compressor | virtual
ColdTempSet | i16 | 4 | 0xEAE3 | 100
HeatTempSet | i16 | 4 | 0xEAE5 | 100
ColdLoopGain | i16 | 4 | 0xEAE4 | 100
HeatLoopGain | i16 | 4 | 0xEAE6 | 100
OutletWaterTemp | i16 | 4 | 0xEAC4 | 100 |  | 0.1
ReturnWaterTemp | i16 | 4 | 0xEAC5 | 100 |  | 0.1
InletTemp | i16 | 4 | 0xEAD4 | 100 |  | 0.1
ExhaustTemp | i16 | 4 | 0xEAD5 | 100 |  | 0.1
AmbientTemp | i16 | 4 | 0xEAC8 | 100 |  | 0.1
OutletWaterPressure | i16 | 4 | 0xEAC6 | 100 |  | 0.1
ReturnWaterPressure | i16 | 4 | 0xEAC7 | 100 |  | 0.1
_fan_speed | u16 | 4 | 0xEAD3 | 100
_pump_speed | u16 | 4 | 0xEAC9 | 100
_comp_speed | u16 | 4 | 0xEACA | 100
PumpIdleProtection | bit | 2 | 0x8A6 | 200
WaterSupplyPumpFault | bit | 2 | 0x8A7 | 200
LiquidTempProbeFault | bit | 2 | 0x8A8 | 200
ReturnLiquidProbeFault | bit | 2 | 0x8A9 | 200
EvapInletProbeFault | bit | 2 | 0x8AA | 200
EvapOutletProbeFault | bit | 2 | 0x8AB | 200
SupplyPressureSensorFault | bit | 2 | 0x8AC | 200
ReturnWaterPressureLow | bit | 2 | 0x8AD | 200
SupplyPressureTooHigh | bit | 2 | 0x8AE | 200
LiquidTempTooHigh | bit | 2 | 0x8AF | 200
ExhaustPressureSensorFault | bit | 2 | 0x8B0 | 200
SystemLowPressure | bit | 2 | 0x8B1 | 200
FanOverload | bit | 2 | 0x8B2 | 200
ScreenMainboardCommTimeout | bit | 2 | 0x8B3 | 200
CompressorInverterCommFault | bit | 2 | 0x8B4 | 200
PumpOvercurrent | bit | 2 | 0x8B5 | 200
PumpDriveOverheat | bit | 2 | 0x8B6 | 200
PumpOvervoltage | bit | 2 | 0x8B7 | 200
PumpUndervoltage | bit | 2 | 0x8B8 | 200
PumpPhaseLoss | bit | 2 | 0x8B9 | 200
ReturnPressureSensorFault | bit | 2 | 0x8BA | 200
PowerLossAlarm | bit | 2 | 0x8BB | 200
SupplyPressureHighAlarm | bit | 2 | 0x8BC | 200
ElectricHeatingProtection | bit | 2 | 0x8BD | 200
VoltageTooHigh | bit | 2 | 0x8BE | 200
SystemHighPressureFault | bit | 2 | 0x8BF | 200
SystemHighPressureLock | bit | 2 | 0x8C0 | 200
MotherboardTtcFault | bit | 2 | 0x8C1 | 200
SlaveBoardCommFault | bit | 2 | 0x8C2 | 200
AmbientProbeFault | bit | 2 | 0x8C3 | 200
PumpStallProtection | bit | 2 | 0x8C4 | 200
VoltageTooLow | bit | 2 | 0x8C5 | 200
LiquidTempTooLow | bit | 2 | 0x8C6 | 200
CompressorStartInstantOc | bit | 2 | 0x8C7 | 200
CompressorAccelOc | bit | 2 | 0x8C8 | 200
CompressorDecelOc | bit | 2 | 0x8C9 | 200
CompressorConstantOc | bit | 2 | 0x8CA | 200
CompressorAccelOv | bit | 2 | 0x8CB | 200
CompressorDecelOv | bit | 2 | 0x8CC | 200
CompressorConstantOv | bit | 2 | 0x8CD | 200
CompressorStandbyOv | bit | 2 | 0x8CE | 200
CompressorRunUv | bit | 2 | 0x8CF | 200
CompressorOutputPhaseLoss | bit | 2 | 0x8D0 | 200
CompressorPowerDeviceProt | bit | 2 | 0x8D1 | 200
CompressorOverheat | bit | 2 | 0x8D2 | 200
CompressorOverload | bit | 2 | 0x8D3 | 200
CompressorDetectsOverload | bit | 2 | 0x8D4 | 200
CompressorLoadHeavy | bit | 2 | 0x8D5 | 200
CompressorSpeedHigh | bit | 2 | 0x8D6 | 200
CompressorDAxisOc | bit | 2 | 0x8D7 | 200
CompressorQAxisOc | bit | 2 | 0x8D8 | 200
CompressorSelfTuneFail | bit | 2 | 0x8D9 | 200
CompressorCommAbnormal | bit | 2 | 0x8DA | 200
CompressorCurrentDetectFault | bit | 2 | 0x8DB | 200
CompressorStartMotorStall | bit | 2 | 0x8DC | 200
CompressorRunMotorStall | bit | 2 | 0x8DD | 200
CompressorStallFault | bit | 2 | 0x8DE | 200
CompressorThermalCutout1 | bit | 2 | 0x8DF | 200
CompressorThermalCutout2 | bit | 2 | 0x8E0 | 200
CompressorStartRotorJitter | bit | 2 | 0x8E1 | 200
CompressorRunRotorJitter | bit | 2 | 0x8E2 | 200
PfcOvercurrent | bit | 2 | 0x8E3 | 200
PfcPeakOvercurrent | bit | 2 | 0x8E4 | 200
PfcRmsOvercurrent | bit | 2 | 0x8E5 | 200
FanStartInstantOc | bit | 2 | 0x8E6 | 200
FanAccelOc | bit | 2 | 0x8E7 | 200
FanDecelOc | bit | 2 | 0x8E8 | 200
FanConstantOc | bit | 2 | 0x8E9 | 200
FanAccelOv | bit | 2 | 0x8EA | 200
FanDecelOv | bit | 2 | 0x8EB | 200
FanConstantOv | bit | 2 | 0x8EC | 200
FanStandbyOv | bit | 2 | 0x8ED | 200
FanRunUv | bit | 2 | 0x8EE | 200
FanInputPhaseLoss | bit | 2 | 0x8EF | 200
FanOutputPhaseLoss | bit | 2 | 0x8F0 | 200
FanPowerDeviceProt | bit | 2 | 0x8F1 | 200
FanOverheat | bit | 2 | 0x8F2 | 200
InverterOverload | bit | 2 | 0x8F3 | 200
FanOverloadVfd | bit | 2 | 0x8F4 | 200
ExternalFault | bit | 2 | 0x8F5 | 200
MotorLoadHeavy | bit | 2 | 0x8F6 | 200
InverterUnderload | bit | 2 | 0x8F7 | 200
FanFault | bit | 2 | 0x8F8 | 200
ProhibitTimeReached | bit | 2 | 0x8F9 | 200
ParamStorageFailed | bit | 2 | 0x8FA | 200
CommAbnormal | bit | 2 | 0x8FB | 200
CurrentDetectFault | bit | 2 | 0x8FC | 200
PoorSelfTuning | bit | 2 | 0x8FD | 200
AnalogInputDisconnect | bit | 2 | 0x8FE | 200
PgWireBreak | bit | 2 | 0x8FF | 200
ThermistorOpen | bit | 2 | 0x900 | 200
AbnormalShutdown | bit | 2 | 0x901 | 200

## bamu_bms
name | type | fc | address | cluster_stride | bit | scale | bias | pt_exp | ct_exp
Online | virtual_comm
TotalVoltage | u16 | 4 | 0x73 | 3000 |  | 0.1
TotalCurrent | i16 | 4 | 0x74 | 3000 |  | 0.1 | -1600
Power | virtual
SOC | u16 | 4 | 0x76 | 3000
SOH | u16 | 4 | 0x77 | 3000
AvgVoltage | u16 | 4 | 0x79 | 3000 |  | 0.001
AvgTemp | u16 | 4 | 0x7a | 3000 |  |  | -40
MaxVoltage | u16 | 4 | 0x7b | 3000 |  | 0.001
MaxVoltageID | u16 | 4 | 0x7c | 3000
MinVoltage | u16 | 4 | 0x7d | 3000 |  | 0.001
MinVoltageID | u16 | 4 | 0x7e | 3000
MaxTemp | u16 | 4 | 0x7f | 3000 |  |  | -40
MaxTempID | u16 | 4 | 0x80 | 3000
MinTemp | u16 | 4 | 0x81 | 3000 |  |  | -40
MinTempID | u16 | 4 | 0x82 | 3000
InsulationResistance | u16 | 4 | 0x78 | 3000
DI1Feedback_positiveContactor | u16 | 4 | 0x6b | 3000
DI2Feedback_fuse | u16 | 4 | 0x6c | 3000
DI3Feedback_negativeContactor | u16 | 4 | 0x6d | 3000
DI4Feedback_breaker | u16 | 4 | 0x70 | 3000
Temp | u16 | 4 | 0x75 | 3000 |  |  | -40
MaxChargePower | u16 | 4 | 0x65 | 3000 |  | 0.1
MaxDishargePower | u16 | 4 | 0x66 | 3000 |  | 0.1
MaxChargeVol | u16 | 4 | 0x67 | 3000 |  | 0.1
MaxDishargeVol | u16 | 4 | 0x68 | 3000 |  | 0.1
MaxChargeCurr | u16 | 4 | 0x69 | 3000 |  | 0.1
MaxDishargeCurr | u16 | 4 | 0x6a | 3000 |  | 0.1
AlarmCommError | bit | 2 | 0xc8 | 100
GroupUnderVolAlarm1 | bit | 2 | 0xc9 | 100
GroupUnderVolAlarm2 | bit | 2 | 0xca | 100
GroupUnderVolAlarm3 | bit | 2 | 0xcb | 100
GroupOverVolAlarm1 | bit | 2 | 0xcc | 100
GroupOverVolAlarm2 | bit | 2 | 0xcd | 100
GroupOverVolAlarm3 | bit | 2 | 0xce | 100
GroupOverCurrAlarm1 | bit | 2 | 0xcf | 100
GroupOverCurrAlarm2 | bit | 2 | 0xd0 | 100
GroupOverCurrAlarm3 | bit | 2 | 0xd1 | 100
CellUnderVolAlarm1 | bit | 2 | 0xd2 | 100
CellUnderVolAlarm2 | bit | 2 | 0xd3 | 100
CellUnderVolAlarm3 | bit | 2 | 0xd4 | 100
CellOverVolAlarm1 | bit | 2 | 0xd5 | 100
CellOverVolAlarm2 | bit | 2 | 0xd6 | 100
CellOverVolAlarm3 | bit | 2 | 0xd7 | 100
CellUnderTempAlarm1 | bit | 2 | 0xd8 | 100
CellUnderTempAlarm2 | bit | 2 | 0xd9 | 100
CellUnderTempAlarm3 | bit | 2 | 0xda | 100
CellOverTempAlarm1 | bit | 2 | 0xdb | 100
CellOverTempAlarm2 | bit | 2 | 0xdc | 100
CellOverTempAlarm3 | bit | 2 | 0xdd | 100
SOCLowAlarm1 | bit | 2 | 0xde | 100
SOCLowAlarm2 | bit | 2 | 0xdf | 100
SOCLowAlarm3 | bit | 2 | 0xe0 | 100
SOCHighAlarm1 | bit | 2 | 0xe1 | 100
SOCHighAlarm2 | bit | 2 | 0xe2 | 100
SOCHighAlarm3 | bit | 2 | 0xe3 | 100
SOHLowAlarm1 | bit | 2 | 0xe4 | 100
SOHLowAlarm2 | bit | 2 | 0xe5 | 100
SOHLowAlarm3 | bit | 2 | 0xe6 | 100
CellVolDiffAlarm1 | bit | 2 | 0xe7 | 100
CellVolDiffAlarm2 | bit | 2 | 0xe8 | 100
CellVolDiffAlarm3 | bit | 2 | 0xe9 | 100
CellTempDiffAlarm1 | bit | 2 | 0xea | 100
CellTempDiffAlarm2 | bit | 2 | 0xeb | 100
CellTempDiffAlarm3 | bit | 2 | 0xec | 100
GroupOverTempAlarm1 | bit | 2 | 0x115 | 100
GroupOverTempAlarm2 | bit | 2 | 0x116 | 100
GroupOverTempAlarm3 | bit | 2 | 0x117 | 100
ModuleUnderVolAlarm1 | bit | 2 | 0x11b | 100
ModuleUnderVolAlarm2 | bit | 2 | 0x11c | 100
ModuleUnderVolAlarm3 | bit | 2 | 0x11d | 100
ModuleOverVolAlarm1 | bit | 2 | 0x118 | 100
ModuleOverVolAlarm2 | bit | 2 | 0x119 | 100
ModuleOverVolAlarm3 | bit | 2 | 0x11a | 100
VolCollectDisconnectAlarm | bit | 2 | 0x11e | 100
CurrCollectDisconnectAlarm | bit | 2 | 0x11f | 100

## bamu_stack
name | type | fc | address | cluster_stride | bit | scale | bias | pt_exp | ct_exp
Online | virtual_comm
SOC | u16 | 4 | 4
SOH | u16 | 4 | 5
TotalVoltage | u16 | 4 | 2 |  |  | 0.1
TotalCurrent | u16 | 4 | 3 |  |  | 0.1 | -1600
ActivePower | virtual
MaxVoltage | u16 | 4 | 6 |  |  | 0.001
MaxVoltageCluster | u16 | 4 | 7
MaxVoltageID | u16 | 4 | 8
MinVoltage | u16 | 4 | 9 |  |  | 0.001
MinVoltageCluster | u16 | 4 | 10
MinVoltageID | u16 | 4 | 11
MaxTemp | u16 | 4 | 12 |  |  |  | -40
MaxTempCluster | u16 | 4 | 13
MaxTempID | u16 | 4 | 14
MinTemp | u16 | 4 | 15 |  |  |  | -40
MinTempCluster | u16 | 4 | 16
MinTempID | u16 | 4 | 17
ChargeEnergy | u32_hi_lo | 4 | 18 |  |  | 0.1
DischargeEnergy | u32_hi_lo | 4 | 20 |  |  | 0.1
OnceChargeEnergy | u32_hi_lo | 4 | 22 |  |  | 0.1
OnceDischargeEnergy | u32_hi_lo | 4 | 24 |  |  | 0.1
DailyChargeEnergy | u32_hi_lo | 4 | 0x26 |  |  | 0.1
DailyDischargeEnergy | u32_hi_lo | 4 | 0x28 |  |  | 0.1
MaxChargePower | u16 | 4 | 0x21 |  |  | 0.1
MaxDischargePower | u16 | 4 | 0x20 |  |  | 0.1
MaxChargeCurr | u16 | 4 | 0x23 |  |  | 0.1
MaxDischargeCurr | u16 | 4 | 0x22 |  |  | 0.1
Temp | u16 | 4 | 0x2A |  |  |  | -40
Status | u16 | 4 | 0x2B
InsulationResistance | u16 | 4 | 0x2D
AlarmLevel | virtual
GroupUnderVolAlarm1 | bit | 2 | 1
GroupUnderVolAlarm2 | bit | 2 | 2
GroupUnderVolAlarm3 | bit | 2 | 3
GroupOverVolAlarm1 | bit | 2 | 4
GroupOverVolAlarm2 | bit | 2 | 5
GroupOverVolAlarm3 | bit | 2 | 6
GroupOverCurrAlarm1 | bit | 2 | 7
GroupOverCurrAlarm2 | bit | 2 | 8
GroupOverCurrAlarm3 | bit | 2 | 9
InsulationLowAlarm1 | bit | 2 | 10
InsulationLowAlarm2 | bit | 2 | 11
InsulationLowAlarm3 | bit | 2 | 12
ModuleUnderTempAlarm1 | bit | 2 | 13
ModuleUnderTempAlarm2 | bit | 2 | 14
ModuleUnderTempAlarm3 | bit | 2 | 15
ModuleOverTempAlarm1 | bit | 2 | 16
ModuleOverTempAlarm2 | bit | 2 | 17
ModuleOverTempAlarm3 | bit | 2 | 18
CellOverVolAlarm1 | bit | 2 | 19
CellOverVolAlarm2 | bit | 2 | 20
CellOverVolAlarm3 | bit | 2 | 21
CellUnderVolAlarm1 | bit | 2 | 22
CellUnderVolAlarm2 | bit | 2 | 23
CellUnderVolAlarm3 | bit | 2 | 24
CellVolDiffAlarm1 | bit | 2 | 25
CellVolDiffAlarm2 | bit | 2 | 26
CellVolDiffAlarm3 | bit | 2 | 27
CellUnderTempAlarm1 | bit | 2 | 28
CellUnderTempAlarm2 | bit | 2 | 29
CellUnderTempAlarm3 | bit | 2 | 30
CellOverTempAlarm1 | bit | 2 | 31
CellOverTempAlarm2 | bit | 2 | 0x20
CellOverTempAlarm3 | bit | 2 | 0x21
CellTempDiffAlarm1 | bit | 2 | 0x22
CellTempDiffAlarm2 | bit | 2 | 0x23
CellTempDiffAlarm3 | bit | 2 | 0x24
SOCLowAlarm1 | bit | 2 | 0x25
SOCLowAlarm2 | bit | 2 | 0x26
SOCLowAlarm3 | bit | 2 | 0x27
SOCHighAlarm1 | bit | 2 | 0x28
SOCHighAlarm2 | bit | 2 | 0x29
SOCHighAlarm3 | bit | 2 | 0x2A
SOHLowAlarm1 | bit | 2 | 0x2B
SOHLowAlarm2 | bit | 2 | 0x2C
SOHLowAlarm3 | bit | 2 | 0x2D
MasterDisconnectAlarm | bit | 2 | 0x31
SlaveDisconnectAlarm | bit | 2 | 0x32
GroupVolAbnormalAlarm | bit | 2 | 0x33
ContactorBreakAbnormalAlarm | bit | 2 | 0x34
ContactorCloseAbnormalAlarm | bit | 2 | 0x35
ChargeStopAlarm | bit | 2 | 0x36
DischargeStopAlarm | bit | 2 | 0x37
GroupOverTempAlarm1 | bit | 2 | 0x46
GroupOverTempAlarm2 | bit | 2 | 0x47
GroupOverTempAlarm3 | bit | 2 | 0x48
ModuleOverVolAlarm1 | bit | 2 | 0x4C
ModuleOverVolAlarm2 | bit | 2 | 0x4D
ModuleOverVolAlarm3 | bit | 2 | 0x4E
ModuleUnderVolAlarm1 | bit | 2 | 0x49
ModuleUnderVolAlarm2 | bit | 2 | 0x4A
ModuleUnderVolAlarm3 | bit | 2 | 0x4B
VolCollectDisconnectAlarm | bit | 2 | 0x4F
CurrCollectDisconnectAlarm | bit | 2 | 0x50
Fault | bit | 2 | 0x39

## dido
name | type | fc | address | cluster_stride | bit | scale | bias | pt_exp | ct_exp
ChiFa_Switch_DI | u16 | 3 | 0x64
PV_Switch_DI | u16 | 3 | 0x65
Load_Switch_DI | u16 | 3 | 0x66
ChiFa_Singn_DI | u16 | 3 | 0x67
YellowLight | virtual
GreenLight | virtual
RedLight | virtual
ChiFa_Switch_DO | virtual
QacSplit | virtual

## pcs_smarten
name | type | fc | address | cluster_stride | bit | scale | bias | pt_exp | ct_exp
Online | virtual_comm
Status | virtual
OnGrid | virtual
APhaseVoltage | i16 | 3 | 0x9D08 |  |  | 0.1
BPhaseVoltage | i16 | 3 | 0x9D1F |  |  | 0.1
CPhaseVoltage | i16 | 3 | 0x9D36 |  |  | 0.1
APhaseCurrent | i16 | 3 | 0x9D07 |  |  | 0.1
BPhaseCurrent | i16 | 3 | 0x9D1E |  |  | 0.1
CPhaseCurrent | i16 | 3 | 0x9D35 |  |  | 0.1
APhasePower | i16 | 3 | 0x9D03 |  |  | 0.1
BPhasePower | i16 | 3 | 0x9D1A |  |  | 0.1
CPhasePower | i16 | 3 | 0x9D31 |  |  | 0.1
APhaseApparentPower | i16 | 3 | 0x9D04 |  |  | 0.1
BPhaseApparentPower | i16 | 3 | 0x9D1B |  |  | 0.1
CPhaseApparentPower | i16 | 3 | 0x9D32 |  |  | 0.1
APhaseReactivePower | i16 | 3 | 0x9D05 |  |  | 0.1
BPhaseReactivePower | i16 | 3 | 0x9D1C |  |  | 0.1
CPhaseReactivePower | i16 | 3 | 0x9D33 |  |  | 0.1
APhasePowerFactor | i16 | 3 | 0x9D06 |  |  | 0.01
BPhasePowerFactor | i16 | 3 | 0x9D1D |  |  | 0.01
CPhasePowerFactor | i16 | 3 | 0x9D34 |  |  | 0.01
ACActivePower | i16 | 3 | 0x9CE4 |  |  | 0.1
ACApparentPower | i16 | 3 | 0x9CE5 |  |  | 0.1
ACReactivePower | i16 | 3 | 0x9CE6 |  |  | 0.1
ACPowerFactor | i16 | 3 | 0x9CE7 |  |  | 0.01
ACFrequency | u32_hi_lo | 3 | 0x9CEB |  |  | 0.01
ModuleTemperature | i16 | 3 | 0x9D01 |  |  | 1
AmbientTemperature | i16 | 3 | 0x9CFD |  |  | 1
CabinetTemperature | i16 | 3 | 0x9CFE |  |  | 1
DCPower | i16 | 3 | 0xA372 |  |  | 0.1
DCCurrent | i16 | 3 | 0xA373 |  |  | 0.1
DCInputVoltage | i16 | 3 | 0xA374 |  |  | 0.1
DCDischargeEnergy | virtual
DCChargeEnergy | virtual
GridABLineVoltage | i16 | 3 | 0xA3BD |  |  | 0.1
GridBCLineVoltage | i16 | 3 | 0xA3BE |  |  | 0.1
GridCALineVoltage | i16 | 3 | 0xA3BF |  |  | 0.1
GridAPhaseCurrent | i16 | 3 | 0xA3A9 |  |  | 0.1
GridBPhaseCurrent | i16 | 3 | 0xA3B1 |  |  | 0.1
GridCPhaseCurrent | i16 | 3 | 0xA3B9 |  |  | 0.1
GridAPhasePower | i16 | 3 | 0xA3A6 |  |  | 0.1
GridBPhasePower | i16 | 3 | 0xA3AE |  |  | 0.1
GridCPhasePower | i16 | 3 | 0xA3B6 |  |  | 0.1
GridAPhaseApparentPower | i16 | 3 | 0xA3A8 |  |  | 0.1
GridBPhaseApparentPower | i16 | 3 | 0xA3B0 |  |  | 0.1
GridCPhaseApparentPower | i16 | 3 | 0xA3B8 |  |  | 0.1
GridAPhaseReactivePower | i16 | 3 | 0xA3A7 |  |  | 0.1
GridBPhaseReactivePower | i16 | 3 | 0xA3AF |  |  | 0.1
GridCPhaseReactivePower | i16 | 3 | 0xA3B7 |  |  | 0.1
GridAPhasePowerFactor | i16 | 3 | 0xA3A5 |  |  | 0.01
GridBPhasePowerFactor | i16 | 3 | 0xA3AD |  |  | 0.01
GridCPhasePowerFactor | i16 | 3 | 0xA3B5 |  |  | 0.01
GridTotalActivePower | i16 | 3 | 0xA39E |  |  | 0.1
GridTotalReactivePower | i16 | 3 | 0xA39F |  |  | 0.1
GridTotalApparentPower | i16 | 3 | 0xA3A0 |  |  | 0.1
GridTotalPowerFactor | i16 | 3 | 0xA39D |  |  | 0.01
GridFrequency | i16 | 3 | 0xA3A1 |  |  | 0.01
LoadABLineVoltage | i16 | 3 | 0xA3EE |  |  | 0.1
LoadBCLineVoltage | i16 | 3 | 0xA3EF |  |  | 0.1
LoadCALineVoltage | i16 | 3 | 0xA3F0 |  |  | 0.1
LoadAPhaseCurrent | i16 | 3 | 0xA3E3 |  |  | 0.1
LoadBPhaseCurrent | i16 | 3 | 0xA3E8 |  |  | 0.1
LoadCPhaseCurrent | i16 | 3 | 0xA3ED |  |  | 0.1
LoadAPhasePower | i16 | 3 | 0xA3E0 |  |  | 0.1
LoadBPhasePower | i16 | 3 | 0xA3E5 |  |  | 0.1
LoadCPhasePower | i16 | 3 | 0xA3EA |  |  | 0.1
LoadAPhaseApparentPower | i16 | 3 | 0xA3E2 |  |  | 0.1
LoadBPhaseApparentPower | i16 | 3 | 0xA3E7 |  |  | 0.1
LoadCPhaseApparentPower | i16 | 3 | 0xA3EC |  |  | 0.1
LoadAPhaseReactivePower | i16 | 3 | 0xA3E1 |  |  | 0.1
LoadBPhaseReactivePower | i16 | 3 | 0xA3E6 |  |  | 0.1
LoadCPhaseReactivePower | i16 | 3 | 0xA3EB |  |  | 0.1
LoadAPhasePowerFactor | i16 | 3 | 0xA3DF |  |  | 0.01
LoadBPhasePowerFactor | i16 | 3 | 0xA3E4 |  |  | 0.01
LoadCPhasePowerFactor | i16 | 3 | 0xA3E9 |  |  | 0.01
LoadTotalActivePower | i16 | 3 | 0xA3DB |  |  | 0.1
LoadTotalApparentPower | i16 | 3 | 0xA3DD |  |  | 0.1
LoadTotalReactivePower | i16 | 3 | 0xA3DC |  |  | 0.1
LoadTotalPowerFactor | i16 | 3 | 0xA3DA |  |  | 0.01
LoadFrequency | i16 | 3 | 0xA3DE |  |  | 0.01
ACDischargeEnergy | virtual
ACChargeEnergy | virtual
DroopState | reg_bit | 3 | 0xA2FF |  | 1
SynchronizationState | reg_bit | 3 | 0xA2FF |  | 2
SynchronizationDoneState | reg_bit | 3 | 0xA2FF |  | 3
FaultState | reg_bit | 3 | 0xA2FD |  | 0
AlarmState | reg_bit | 3 | 0xA2FD |  | 1
TotalFanFault | reg_bit | 3 | 0xA2FD |  | 2
TotalAuxPowerFault | reg_bit | 3 | 0xA2FD |  | 3
TotalOverTemperatureFault | reg_bit | 3 | 0xA2FD |  | 4
TotalModuleOverCurrentFault | reg_bit | 3 | 0xA2FD |  | 5
TotalModuleCurrentLimitAlarm | reg_bit | 3 | 0xA2FD |  | 6
AmbientOverTemperatureFault | reg_bit | 3 | 0xA2FD |  | 7
ModuleCurrentUnbalanceFault | reg_bit | 3 | 0xA2FD |  | 8
EmergencyShutdown | reg_bit | 3 | 0xA300 |  | 0
DspInitializingAbnormal | reg_bit | 3 | 0xA301 |  | 0
DspVersionAbnormal | reg_bit | 3 | 0xA301 |  | 1
DspParameterMismatch | reg_bit | 3 | 0xA301 |  | 2
CpldVersionAbnormal | reg_bit | 3 | 0xA301 |  | 3
FlashAbnormal | reg_bit | 3 | 0xA301 |  | 4
MonitorInitializingAbnormal | reg_bit | 3 | 0xA302 |  | 0
MonitorParameterMismatch | reg_bit | 3 | 0xA302 |  | 1
HardwareVersionError | reg_bit | 3 | 0xA303 |  | 0
IdReduplicatedFault | reg_bit | 3 | 0xA303 |  | 1
CalibrationParameterError | reg_bit | 3 | 0xA304 |  | 0
SamplingZeroPointError | reg_bit | 3 | 0xA304 |  | 1
CanACommunicationFault | reg_bit | 3 | 0xA305 |  | 0
CanBCommunicationFault | reg_bit | 3 | 0xA305 |  | 1
CanCCommunicationFault | reg_bit | 3 | 0xA305 |  | 2
CanDCommunicationFault | reg_bit | 3 | 0xA305 |  | 3
Rs485_1CommunicationFault | reg_bit | 3 | 0xA305 |  | 4
Rs485_2CommunicationFault | reg_bit | 3 | 0xA305 |  | 5
Rs485_3CommunicationFault | reg_bit | 3 | 0xA305 |  | 6
Rs485_4CommunicationFault | reg_bit | 3 | 0xA305 |  | 7
AuxiliaryBoardCommunicationFault | reg_bit | 3 | 0xA305 |  | 8
SpiCommunicationFault | reg_bit | 3 | 0xA305 |  | 9
EmsCommConnectionTimeout | reg_bit | 3 | 0xA305 |  | 10
Rs485CommunicationFault | reg_bit | 3 | 0xA305 |  | 11
SynchronizationSignal1Fault | reg_bit | 3 | 0xA306 |  | 0
SynchronizationSignal2Fault | reg_bit | 3 | 0xA306 |  | 1
DcInputOvervoltage | reg_bit | 3 | 0xA317 |  | 0
DcInputUndervoltage | reg_bit | 3 | 0xA317 |  | 1
DcInputReverse | reg_bit | 3 | 0xA317 |  | 2
DcOverloadAlarm | reg_bit | 3 | 0xA317 |  | 3
DcOverloadTimeoutFault | reg_bit | 3 | 0xA317 |  | 4
DcInputSoftStartFailure | reg_bit | 3 | 0xA317 |  | 5
DcInputElectricControlSwitchOpenCircuit | reg_bit | 3 | 0xA317 |  | 6
DcInputElectricControlSwitchShortCircuit | reg_bit | 3 | 0xA317 |  | 7
DcInputGalvanicBreakDeviceHardwareFault | reg_bit | 3 | 0xA317 |  | 8
DcInputSoftGalvanicBreakDeviceFault | reg_bit | 3 | 0xA317 |  | 9
DcInputDryContactOpenCircuit | reg_bit | 3 | 0xA317 |  | 10
DcBusOverVoltage | reg_bit | 3 | 0xA318 |  | 0
DcBusUnderVoltage | reg_bit | 3 | 0xA318 |  | 1
DcBusVoltageUnbalanced | reg_bit | 3 | 0xA318 |  | 2
DcBusSoftStartFailed | reg_bit | 3 | 0xA318 |  | 3
DcBusGalvanicBreakDeviceOpenCircuit | reg_bit | 3 | 0xA318 |  | 4
DcBusGalvanicBreakDeviceShortCircuit | reg_bit | 3 | 0xA318 |  | 5
DcBusGalvanicBreakDeviceHardwareFault | reg_bit | 3 | 0xA318 |  | 6
DcBusSoftGalvanicBreakDeviceFault | reg_bit | 3 | 0xA318 |  | 7
DcInsulationDetectAbnormal | reg_bit | 3 | 0xA318 |  | 8
AcBusOverVoltage | reg_bit | 3 | 0xA319 |  | 0
AcBusUnderVoltage | reg_bit | 3 | 0xA319 |  | 1
AcBusOverFrequency | reg_bit | 3 | 0xA319 |  | 2
AcBusUnderFrequency | reg_bit | 3 | 0xA319 |  | 3
AcBusPhaseReversed | reg_bit | 3 | 0xA319 |  | 4
AcBusVoltageUnbalance | reg_bit | 3 | 0xA319 |  | 5
AcBusVoltageAbnormal | reg_bit | 3 | 0xA319 |  | 6
AcBusPhaseLost | reg_bit | 3 | 0xA319 |  | 7
IslandingProtection | reg_bit | 3 | 0xA319 |  | 8
PllFailed | reg_bit | 3 | 0xA319 |  | 9
AcCurrentDcComponentExcess | reg_bit | 3 | 0xA319 |  | 10
AcOverloadAlarm | reg_bit | 3 | 0xA319 |  | 11
AcOverloadTimeout | reg_bit | 3 | 0xA319 |  | 12
AcBusConnectionForbidden | reg_bit | 3 | 0xA319 |  | 13
AcBusNPhaseLoss | reg_bit | 3 | 0xA319 |  | 14
AcSoftStartFailed | reg_bit | 3 | 0xA31A |  | 0
AcGalvanicBreakDeviceOpenCircuit | reg_bit | 3 | 0xA31A |  | 1
AcGalvanicBreakDeviceShortCircuit | reg_bit | 3 | 0xA31A |  | 2
AcGalvanicBreakDeviceHardwareFault | reg_bit | 3 | 0xA31A |  | 3
AcSoftStartGalvanicBreakDeviceFault | reg_bit | 3 | 0xA31A |  | 4
GridOverVoltage | reg_bit | 3 | 0xA396 |  | 0
GridUnderVoltage | reg_bit | 3 | 0xA396 |  | 1
GridOverFrequency | reg_bit | 3 | 0xA396 |  | 2
GridUnderFrequency | reg_bit | 3 | 0xA396 |  | 3
GridPhaseReversed | reg_bit | 3 | 0xA396 |  | 4
GridVoltageUnbalance | reg_bit | 3 | 0xA396 |  | 5
GridVoltageAbnormal | reg_bit | 3 | 0xA396 |  | 6
GridPhaseLoss | reg_bit | 3 | 0xA396 |  | 7
GridNPhaseLoss | reg_bit | 3 | 0xA396 |  | 8
GridPowerDown | reg_bit | 3 | 0xA396 |  | 9
GridConnectionForbidden | reg_bit | 3 | 0xA396 |  | 10
GridOverloadAlarm | reg_bit | 3 | 0xA397 |  | 0
GridOverloadTimeoutFault | reg_bit | 3 | 0xA397 |  | 1
AbnormalOffGridVoltage | reg_bit | 3 | 0xA398 |  | 0
OffGridVoltageOscillation | reg_bit | 3 | 0xA398 |  | 1
OffGridFrequencyAbnormal | reg_bit | 3 | 0xA398 |  | 2
OffGridVoltagePhaseReversed | reg_bit | 3 | 0xA398 |  | 3
OffGridVoltagePhaseLoss | reg_bit | 3 | 0xA398 |  | 4
OffGridSoftStartFailure | reg_bit | 3 | 0xA399 |  | 0
GridOffGridSwitchingError | reg_bit | 3 | 0xA399 |  | 1
TotalDeratingAbnormal | reg_bit | 3 | 0xA312 |  | 0
ModuleOvertempDerating | reg_bit | 3 | 0xA312 |  | 1
CabinetOvertempDerating | reg_bit | 3 | 0xA312 |  | 2
AmbientOvertempDerating | reg_bit | 3 | 0xA312 |  | 3
BmsDryContactChargeForbidden | reg_bit | 3 | 0xA475 |  | 2
BmsDryContactDischargeForbidden | reg_bit | 3 | 0xA475 |  | 3
BmsShutdownFault | reg_bit | 3 | 0xA476 |  | 0
BmsCommConnectionTimeout | reg_bit | 3 | 0xA476 |  | 1
BmsDryContactFault | reg_bit | 3 | 0xA476 |  | 2
_st41726_b1 | reg_bit | 3 | 0xA2FE |  | 1
_st41726_b2 | reg_bit | 3 | 0xA2FE |  | 2
_st41726_b3 | reg_bit | 3 | 0xA2FE |  | 3
_st41726_b4 | reg_bit | 3 | 0xA2FE |  | 4
_st41726_b5 | reg_bit | 3 | 0xA2FE |  | 5
_st41726_b6 | reg_bit | 3 | 0xA2FE |  | 6
_st41726_b7 | reg_bit | 3 | 0xA2FE |  | 7
_st41726_b8 | reg_bit | 3 | 0xA2FE |  | 8
_st41726_b9 | reg_bit | 3 | 0xA2FE |  | 9
_st41726_b10 | reg_bit | 3 | 0xA2FE |  | 10
_st41726_b11 | reg_bit | 3 | 0xA2FE |  | 11
_st41726_b12 | reg_bit | 3 | 0xA2FE |  | 12
_st41727_b4 | reg_bit | 3 | 0xA2FF |  | 4

## sun_pv
name | type | fc | address | cluster_stride | bit | scale | bias | pt_exp | ct_exp
Online | virtual_comm
MPPTStatus | virtual
DailyGeneration | u16 | 4 | 5002 |  |  | 0.1
MonthlyGeneration | u32_lo_hi | 4 | 5127 |  |  | 0.1
TotalGeneration | u32_lo_hi | 4 | 5003
RunningTime | u32_lo_hi | 4 | 5005
AmbientTemperature | i16 | 4 | 5007 |  |  | 0.1
TotalActivePower | u32_lo_hi | 4 | 5030 |  |  | 0.001
TotalReactivePower | u32_lo_hi | 4 | 5032 |  |  | 0.001
TotalApparentPower | u32_lo_hi | 4 | 5008 |  |  | 0.001
DCTotalPower | u32_lo_hi | 4 | 5016 |  |  | 0.001
TotalPowerFactor | i16 | 4 | 5034 |  |  | 0.001
Frequency | u16 | 4 | 5035 |  |  | 0.1
APhaseVoltage | u16 | 4 | 5018 |  |  | 0.1
BPhaseVoltage | u16 | 4 | 5019 |  |  | 0.1
CPhaseVoltage | u16 | 4 | 5020 |  |  | 0.1
APhaseCurrent | i16 | 4 | 5021 |  |  | 0.1
BPhaseCurrent | i16 | 4 | 5022 |  |  | 0.1
CPhaseCurrent | i16 | 4 | 5023 |  |  | 0.1
Mppt1Voltage | u16 | 4 | 5010 |  |  | 0.1
Mppt1Current | i16 | 4 | 5011 |  |  | 0.1
Mppt2Voltage | u16 | 4 | 5012 |  |  | 0.1
Mppt2Current | i16 | 4 | 5013 |  |  | 0.1
Mppt3Voltage | u16 | 4 | 5014 |  |  | 0.1
Mppt3Current | i16 | 4 | 5015 |  |  | 0.1
Mppt4Voltage | u16 | 4 | 5114 |  |  | 0.1
Mppt4Current | i16 | 4 | 5115 |  |  | 0.1
Mppt5Voltage | u16 | 4 | 5116 |  |  | 0.1
Mppt5Current | i16 | 4 | 5117 |  |  | 0.1
Mppt6Voltage | u16 | 4 | 5118 |  |  | 0.1
Mppt6Current | i16 | 4 | 5119 |  |  | 0.1
Mppt7Voltage | u16 | 4 | 5120 |  |  | 0.1
Mppt7Current | i16 | 4 | 5121 |  |  | 0.1
Mppt8Voltage | u16 | 4 | 5122 |  |  | 0.1
Mppt8Current | i16 | 4 | 5123 |  |  | 0.1
Mppt9Voltage | u16 | 4 | 5129 |  |  | 0.1
Mppt9Current | i16 | 4 | 5130 |  |  | 0.1
Mppt10Voltage | u16 | 4 | 5131 |  |  | 0.1
Mppt10Current | i16 | 4 | 5132 |  |  | 0.1
Mppt11Voltage | u16 | 4 | 5133 |  |  | 0.1
Mppt11Current | i16 | 4 | 5134 |  |  | 0.1
Mppt12Voltage | u16 | 4 | 5135 |  |  | 0.1
Mppt12Current | i16 | 4 | 5136 |  |  | 0.1
GridOvervoltage | virtual
GridUndervoltage | virtual
GridOverfrequency | virtual
GridUnderfrequency | virtual
GridPowerOutage | virtual
LeakageCurrentHigh | virtual
GridAbnormality | virtual
GridVoltageUnbalance | virtual
PvBackupConnectionFault | virtual
PvReverseConnectionAlarm | virtual
PvAbnormalityAlarm | virtual
MpptReverseConnection | virtual
BoostCapOvervoltageAlarm | virtual
BoostCapOvervoltageFault | virtual
PvCableShortToGround | virtual
StringCurrentBackflow | virtual
PvGroundingFault | virtual
SystemHardwareFault | virtual
AmbientTempHigh | virtual
AmbientTempLow | virtual
InsulationResistanceLow | virtual
GroundCableFault | virtual
ArcFault | virtual
MeterCtReverseAlarm | virtual
MeterCommAbnormalityAlarm | virtual
GridConflict | virtual
InverterGridTiedCommAlarm | virtual
SystemFault | virtual
SystemAlarm | virtual
PIDImpedanceAbnormal | virtual
PIDFunctionAbnormal | virtual
PIDVoltageCurrentProtection | virtual
_InverterState | u16 | 4 | 5037
_Alarm5044 | u16 | 4 | 5044
_PidCode | u16 | 4 | 5150
_ActivePowerLimit | u16 | 3 | 5007
_pad5024 | u16 | 4 | 5024
_pad5025 | u16 | 4 | 5025
_pad5026 | u16 | 4 | 5026
_pad5027 | u16 | 4 | 5027
_pad5028 | u16 | 4 | 5028
_pad5029 | u16 | 4 | 5029
_pad5124 | u16 | 4 | 5124
_pad5125 | u16 | 4 | 5125
_pad5126 | u16 | 4 | 5126

## 写库映射
template | field_map | name | addr
agc | agc | Online | 0
agc | agc | ABVoltage | 1
agc | agc | BCVoltage | 2
agc | agc | CAVoltage | 3
agc | agc | APhaseVoltage | 4
agc | agc | BPhaseVoltage | 5
agc | agc | CPhaseVoltage | 6
agc | agc | AFrequency | 7
agc | agc | BFrequency | 8
agc | agc | CFrequency | 9
agc | agc | APhaseCurrent | 10
agc | agc | BPhaseCurrent | 11
agc | agc | CPhaseCurrent | 12
agc | agc | APhaseActivePower | 13
agc | agc | BPhaseActivePower | 14
agc | agc | CPhaseActivePower | 15
agc | agc | TotalActivePower | 16
agc | agc | APhaseReactivePower | 17
agc | agc | BPhaseReactivePower | 18
agc | agc | CPhaseReactivePower | 19
agc | agc | TotalReactivePower | 20
agc | agc | APhaseApparentPower | 21
agc | agc | BPhaseApparentPower | 22
agc | agc | CPhaseApparentPower | 23
agc | agc | TotalApparentPower | 24
agc | agc | TotalActiveEnergy | 25
agc | agc | TotalReactiveEnergy | 26
agc | agc | TotalPowerFactor | 27
agc | agc | EngineOilLevel | 28
amc_meter | amc_meter | Online | 0
amc_meter | amc_meter | APhaseVoltage | 1
amc_meter | amc_meter | BPhaseVoltage | 2
amc_meter | amc_meter | CPhaseVoltage | 3
amc_meter | amc_meter | ABVoltage | 4
amc_meter | amc_meter | BCVoltage | 5
amc_meter | amc_meter | CAVoltage | 6
amc_meter | amc_meter | APhaseCurrent | 7
amc_meter | amc_meter | BPhaseCurrent | 8
amc_meter | amc_meter | CPhaseCurrent | 9
amc_meter | amc_meter | APhaseActivePower | 10
amc_meter | amc_meter | BPhaseActivePower | 11
amc_meter | amc_meter | CPhaseActivePower | 12
amc_meter | amc_meter | TotalActivePower | 13
amc_meter | amc_meter | APhaseReactivePower | 14
amc_meter | amc_meter | BPhaseReactivePower | 15
amc_meter | amc_meter | CPhaseReactivePower | 16
amc_meter | amc_meter | TotalReactivePower | 17
amc_meter | amc_meter | APhaseApparentPower | 18
amc_meter | amc_meter | BPhaseApparentPower | 19
amc_meter | amc_meter | CPhaseApparentPower | 20
amc_meter | amc_meter | TotalApparentPower | 21
amc_meter | amc_meter | APowerFactor | 22
amc_meter | amc_meter | BPowerFactor | 23
amc_meter | amc_meter | CPowerFactor | 24
amc_meter | amc_meter | TotalPowerFactor | 25
amc_meter | amc_meter | Frequency | 26
amc_meter | amc_meter | AbsorbActiveEnergyPrimary | 27
amc_meter | amc_meter | ReleaseActiveEnergyPrimary | 28
bamu_air | bamu_air | Online | 0
bamu_air | bamu_air | OnOffStatus | 1
bamu_air | bamu_air | OperationMode | 2
bamu_air | bamu_air | FanStatus | 3
bamu_air | bamu_air | WaterPumpStatus | 4
bamu_air | bamu_air | Compressor | 5
bamu_air | bamu_air | ColdTempSet | 6
bamu_air | bamu_air | HeatTempSet | 7
bamu_air | bamu_air | ColdLoopGain | 8
bamu_air | bamu_air | HeatLoopGain | 9
bamu_air | bamu_air | OutletWaterTemp | 10
bamu_air | bamu_air | ReturnWaterTemp | 11
bamu_air | bamu_air | InletTemp | 12
bamu_air | bamu_air | ExhaustTemp | 13
bamu_air | bamu_air | AmbientTemp | 14
bamu_air | bamu_air | OutletWaterPressure | 15
bamu_air | bamu_air | ReturnWaterPressure | 16
bamu_air | bamu_air | PumpIdleProtection | 17
bamu_air | bamu_air | WaterSupplyPumpFault | 18
bamu_air | bamu_air | LiquidTempProbeFault | 19
bamu_air | bamu_air | ReturnLiquidProbeFault | 20
bamu_air | bamu_air | EvapInletProbeFault | 21
bamu_air | bamu_air | EvapOutletProbeFault | 22
bamu_air | bamu_air | SupplyPressureSensorFault | 23
bamu_air | bamu_air | ReturnWaterPressureLow | 24
bamu_air | bamu_air | SupplyPressureTooHigh | 25
bamu_air | bamu_air | LiquidTempTooHigh | 26
bamu_air | bamu_air | ExhaustPressureSensorFault | 27
bamu_air | bamu_air | SystemLowPressure | 28
bamu_air | bamu_air | FanOverload | 29
bamu_air | bamu_air | ScreenMainboardCommTimeout | 30
bamu_air | bamu_air | CompressorInverterCommFault | 31
bamu_air | bamu_air | PumpOvercurrent | 32
bamu_air | bamu_air | PumpDriveOverheat | 33
bamu_air | bamu_air | PumpOvervoltage | 34
bamu_air | bamu_air | PumpUndervoltage | 35
bamu_air | bamu_air | PumpPhaseLoss | 36
bamu_air | bamu_air | ReturnPressureSensorFault | 37
bamu_air | bamu_air | PowerLossAlarm | 38
bamu_air | bamu_air | SupplyPressureHighAlarm | 39
bamu_air | bamu_air | ElectricHeatingProtection | 40
bamu_air | bamu_air | VoltageTooHigh | 41
bamu_air | bamu_air | SystemHighPressureFault | 42
bamu_air | bamu_air | SystemHighPressureLock | 43
bamu_air | bamu_air | MotherboardTtcFault | 44
bamu_air | bamu_air | SlaveBoardCommFault | 45
bamu_air | bamu_air | AmbientProbeFault | 46
bamu_air | bamu_air | PumpStallProtection | 47
bamu_air | bamu_air | VoltageTooLow | 48
bamu_air | bamu_air | LiquidTempTooLow | 49
bamu_air | bamu_air | CompressorStartInstantOc | 50
bamu_air | bamu_air | CompressorAccelOc | 51
bamu_air | bamu_air | CompressorDecelOc | 52
bamu_air | bamu_air | CompressorConstantOc | 53
bamu_air | bamu_air | CompressorAccelOv | 54
bamu_air | bamu_air | CompressorDecelOv | 55
bamu_air | bamu_air | CompressorConstantOv | 56
bamu_air | bamu_air | CompressorStandbyOv | 57
bamu_air | bamu_air | CompressorRunUv | 58
bamu_air | bamu_air | CompressorOutputPhaseLoss | 59
bamu_air | bamu_air | CompressorPowerDeviceProt | 60
bamu_air | bamu_air | CompressorOverheat | 61
bamu_air | bamu_air | CompressorOverload | 62
bamu_air | bamu_air | CompressorDetectsOverload | 63
bamu_air | bamu_air | CompressorLoadHeavy | 64
bamu_air | bamu_air | CompressorSpeedHigh | 65
bamu_air | bamu_air | CompressorDAxisOc | 66
bamu_air | bamu_air | CompressorQAxisOc | 67
bamu_air | bamu_air | CompressorSelfTuneFail | 68
bamu_air | bamu_air | CompressorCommAbnormal | 69
bamu_air | bamu_air | CompressorCurrentDetectFault | 70
bamu_air | bamu_air | CompressorStartMotorStall | 71
bamu_air | bamu_air | CompressorRunMotorStall | 72
bamu_air | bamu_air | CompressorStallFault | 73
bamu_air | bamu_air | CompressorThermalCutout1 | 74
bamu_air | bamu_air | CompressorThermalCutout2 | 75
bamu_air | bamu_air | CompressorStartRotorJitter | 76
bamu_air | bamu_air | CompressorRunRotorJitter | 77
bamu_air | bamu_air | PfcOvercurrent | 78
bamu_air | bamu_air | PfcPeakOvercurrent | 79
bamu_air | bamu_air | PfcRmsOvercurrent | 80
bamu_air | bamu_air | FanStartInstantOc | 81
bamu_air | bamu_air | FanAccelOc | 82
bamu_air | bamu_air | FanDecelOc | 83
bamu_air | bamu_air | FanConstantOc | 84
bamu_air | bamu_air | FanAccelOv | 85
bamu_air | bamu_air | FanDecelOv | 86
bamu_air | bamu_air | FanConstantOv | 87
bamu_air | bamu_air | FanStandbyOv | 88
bamu_air | bamu_air | FanRunUv | 89
bamu_air | bamu_air | FanInputPhaseLoss | 90
bamu_air | bamu_air | FanOutputPhaseLoss | 91
bamu_air | bamu_air | FanPowerDeviceProt | 92
bamu_air | bamu_air | FanOverheat | 93
bamu_air | bamu_air | InverterOverload | 94
bamu_air | bamu_air | FanOverloadVfd | 95
bamu_air | bamu_air | ExternalFault | 96
bamu_air | bamu_air | MotorLoadHeavy | 97
bamu_air | bamu_air | InverterUnderload | 98
bamu_air | bamu_air | FanFault | 99
bamu_air | bamu_air | ProhibitTimeReached | 100
bamu_air | bamu_air | ParamStorageFailed | 101
bamu_air | bamu_air | CommAbnormal | 102
bamu_air | bamu_air | CurrentDetectFault | 103
bamu_air | bamu_air | PoorSelfTuning | 104
bamu_air | bamu_air | AnalogInputDisconnect | 105
bamu_air | bamu_air | PgWireBreak | 106
bamu_air | bamu_air | ThermistorOpen | 107
bamu_air | bamu_air | AbnormalShutdown | 108
bamu_bms | bamu_bms | Online | 0
bamu_bms | bamu_bms | TotalVoltage | 1
bamu_bms | bamu_bms | TotalCurrent | 2
bamu_bms | bamu_bms | Power | 3
bamu_bms | bamu_bms | SOC | 4
bamu_bms | bamu_bms | SOH | 5
bamu_bms | bamu_bms | AvgVoltage | 6
bamu_bms | bamu_bms | AvgTemp | 7
bamu_bms | bamu_bms | MaxVoltage | 8
bamu_bms | bamu_bms | MaxVoltageID | 9
bamu_bms | bamu_bms | MinVoltage | 10
bamu_bms | bamu_bms | MinVoltageID | 11
bamu_bms | bamu_bms | MaxTemp | 12
bamu_bms | bamu_bms | MaxTempID | 13
bamu_bms | bamu_bms | MinTemp | 14
bamu_bms | bamu_bms | MinTempID | 15
bamu_bms | bamu_bms | InsulationResistance | 16
bamu_bms | bamu_bms | DI1Feedback_positiveContactor | 17
bamu_bms | bamu_bms | DI2Feedback_fuse | 18
bamu_bms | bamu_bms | DI3Feedback_negativeContactor | 19
bamu_bms | bamu_bms | DI4Feedback_breaker | 20
bamu_bms | bamu_bms | Temp | 21
bamu_bms | bamu_bms | MaxChargePower | 22
bamu_bms | bamu_bms | MaxDishargePower | 23
bamu_bms | bamu_bms | MaxChargeVol | 24
bamu_bms | bamu_bms | MaxDishargeVol | 25
bamu_bms | bamu_bms | MaxChargeCurr | 26
bamu_bms | bamu_bms | MaxDishargeCurr | 27
bamu_bms | bamu_bms | AlarmCommError | 28
bamu_bms | bamu_bms | GroupUnderVolAlarm1 | 29
bamu_bms | bamu_bms | GroupUnderVolAlarm2 | 30
bamu_bms | bamu_bms | GroupUnderVolAlarm3 | 31
bamu_bms | bamu_bms | GroupOverVolAlarm1 | 32
bamu_bms | bamu_bms | GroupOverVolAlarm2 | 33
bamu_bms | bamu_bms | GroupOverVolAlarm3 | 34
bamu_bms | bamu_bms | GroupOverCurrAlarm1 | 35
bamu_bms | bamu_bms | GroupOverCurrAlarm2 | 36
bamu_bms | bamu_bms | GroupOverCurrAlarm3 | 37
bamu_bms | bamu_bms | CellUnderVolAlarm1 | 38
bamu_bms | bamu_bms | CellUnderVolAlarm2 | 39
bamu_bms | bamu_bms | CellUnderVolAlarm3 | 40
bamu_bms | bamu_bms | CellOverVolAlarm1 | 41
bamu_bms | bamu_bms | CellOverVolAlarm2 | 42
bamu_bms | bamu_bms | CellOverVolAlarm3 | 43
bamu_bms | bamu_bms | CellUnderTempAlarm1 | 44
bamu_bms | bamu_bms | CellUnderTempAlarm2 | 45
bamu_bms | bamu_bms | CellUnderTempAlarm3 | 46
bamu_bms | bamu_bms | CellOverTempAlarm1 | 47
bamu_bms | bamu_bms | CellOverTempAlarm2 | 48
bamu_bms | bamu_bms | CellOverTempAlarm3 | 49
bamu_bms | bamu_bms | SOCLowAlarm1 | 50
bamu_bms | bamu_bms | SOCLowAlarm2 | 51
bamu_bms | bamu_bms | SOCLowAlarm3 | 52
bamu_bms | bamu_bms | SOCHighAlarm1 | 53
bamu_bms | bamu_bms | SOCHighAlarm2 | 54
bamu_bms | bamu_bms | SOCHighAlarm3 | 55
bamu_bms | bamu_bms | SOHLowAlarm1 | 56
bamu_bms | bamu_bms | SOHLowAlarm2 | 57
bamu_bms | bamu_bms | SOHLowAlarm3 | 58
bamu_bms | bamu_bms | CellVolDiffAlarm1 | 59
bamu_bms | bamu_bms | CellVolDiffAlarm2 | 60
bamu_bms | bamu_bms | CellVolDiffAlarm3 | 61
bamu_bms | bamu_bms | CellTempDiffAlarm1 | 62
bamu_bms | bamu_bms | CellTempDiffAlarm2 | 63
bamu_bms | bamu_bms | CellTempDiffAlarm3 | 64
bamu_bms | bamu_bms | GroupOverTempAlarm1 | 65
bamu_bms | bamu_bms | GroupOverTempAlarm2 | 66
bamu_bms | bamu_bms | GroupOverTempAlarm3 | 67
bamu_bms | bamu_bms | ModuleUnderVolAlarm1 | 68
bamu_bms | bamu_bms | ModuleUnderVolAlarm2 | 69
bamu_bms | bamu_bms | ModuleUnderVolAlarm3 | 70
bamu_bms | bamu_bms | ModuleOverVolAlarm1 | 71
bamu_bms | bamu_bms | ModuleOverVolAlarm2 | 72
bamu_bms | bamu_bms | ModuleOverVolAlarm3 | 73
bamu_bms | bamu_bms | VolCollectDisconnectAlarm | 74
bamu_bms | bamu_bms | CurrCollectDisconnectAlarm | 75
bamu_stack | bamu_stack | Online | 0
bamu_stack | bamu_stack | SOC | 1
bamu_stack | bamu_stack | SOH | 2
bamu_stack | bamu_stack | TotalVoltage | 3
bamu_stack | bamu_stack | TotalCurrent | 4
bamu_stack | bamu_stack | ActivePower | 5
bamu_stack | bamu_stack | MaxVoltage | 6
bamu_stack | bamu_stack | MaxVoltageCluster | 7
bamu_stack | bamu_stack | MaxVoltageID | 8
bamu_stack | bamu_stack | MinVoltage | 9
bamu_stack | bamu_stack | MinVoltageCluster | 10
bamu_stack | bamu_stack | MinVoltageID | 11
bamu_stack | bamu_stack | MaxTemp | 12
bamu_stack | bamu_stack | MaxTempCluster | 13
bamu_stack | bamu_stack | MaxTempID | 14
bamu_stack | bamu_stack | MinTemp | 15
bamu_stack | bamu_stack | MinTempCluster | 16
bamu_stack | bamu_stack | MinTempID | 17
bamu_stack | bamu_stack | ChargeEnergy | 18
bamu_stack | bamu_stack | DischargeEnergy | 19
bamu_stack | bamu_stack | OnceChargeEnergy | 20
bamu_stack | bamu_stack | OnceDischargeEnergy | 21
bamu_stack | bamu_stack | DailyChargeEnergy | 22
bamu_stack | bamu_stack | DailyDischargeEnergy | 23
bamu_stack | bamu_stack | MaxChargePower | 24
bamu_stack | bamu_stack | MaxDischargePower | 25
bamu_stack | bamu_stack | MaxChargeCurr | 26
bamu_stack | bamu_stack | MaxDischargeCurr | 27
bamu_stack | bamu_stack | Temp | 28
bamu_stack | bamu_stack | Status | 29
bamu_stack | bamu_stack | InsulationResistance | 30
bamu_stack | bamu_stack | AlarmLevel | 31
bamu_stack | bamu_stack | GroupUnderVolAlarm1 | 32
bamu_stack | bamu_stack | GroupUnderVolAlarm2 | 33
bamu_stack | bamu_stack | GroupUnderVolAlarm3 | 34
bamu_stack | bamu_stack | GroupOverVolAlarm1 | 35
bamu_stack | bamu_stack | GroupOverVolAlarm2 | 36
bamu_stack | bamu_stack | GroupOverVolAlarm3 | 37
bamu_stack | bamu_stack | GroupOverCurrAlarm1 | 38
bamu_stack | bamu_stack | GroupOverCurrAlarm2 | 39
bamu_stack | bamu_stack | GroupOverCurrAlarm3 | 40
bamu_stack | bamu_stack | InsulationLowAlarm1 | 41
bamu_stack | bamu_stack | InsulationLowAlarm2 | 42
bamu_stack | bamu_stack | InsulationLowAlarm3 | 43
bamu_stack | bamu_stack | ModuleUnderTempAlarm1 | 44
bamu_stack | bamu_stack | ModuleUnderTempAlarm2 | 45
bamu_stack | bamu_stack | ModuleUnderTempAlarm3 | 46
bamu_stack | bamu_stack | ModuleOverTempAlarm1 | 47
bamu_stack | bamu_stack | ModuleOverTempAlarm2 | 48
bamu_stack | bamu_stack | ModuleOverTempAlarm3 | 49
bamu_stack | bamu_stack | CellOverVolAlarm1 | 50
bamu_stack | bamu_stack | CellOverVolAlarm2 | 51
bamu_stack | bamu_stack | CellOverVolAlarm3 | 52
bamu_stack | bamu_stack | CellUnderVolAlarm1 | 53
bamu_stack | bamu_stack | CellUnderVolAlarm2 | 54
bamu_stack | bamu_stack | CellUnderVolAlarm3 | 55
bamu_stack | bamu_stack | CellVolDiffAlarm1 | 56
bamu_stack | bamu_stack | CellVolDiffAlarm2 | 57
bamu_stack | bamu_stack | CellVolDiffAlarm3 | 58
bamu_stack | bamu_stack | CellUnderTempAlarm1 | 59
bamu_stack | bamu_stack | CellUnderTempAlarm2 | 60
bamu_stack | bamu_stack | CellUnderTempAlarm3 | 61
bamu_stack | bamu_stack | CellOverTempAlarm1 | 62
bamu_stack | bamu_stack | CellOverTempAlarm2 | 63
bamu_stack | bamu_stack | CellOverTempAlarm3 | 64
bamu_stack | bamu_stack | CellTempDiffAlarm1 | 65
bamu_stack | bamu_stack | CellTempDiffAlarm2 | 66
bamu_stack | bamu_stack | CellTempDiffAlarm3 | 67
bamu_stack | bamu_stack | SOCLowAlarm1 | 68
bamu_stack | bamu_stack | SOCLowAlarm2 | 69
bamu_stack | bamu_stack | SOCLowAlarm3 | 70
bamu_stack | bamu_stack | SOCHighAlarm1 | 71
bamu_stack | bamu_stack | SOCHighAlarm2 | 72
bamu_stack | bamu_stack | SOCHighAlarm3 | 73
bamu_stack | bamu_stack | SOHLowAlarm1 | 74
bamu_stack | bamu_stack | SOHLowAlarm2 | 75
bamu_stack | bamu_stack | SOHLowAlarm3 | 76
bamu_stack | bamu_stack | MasterDisconnectAlarm | 77
bamu_stack | bamu_stack | SlaveDisconnectAlarm | 78
bamu_stack | bamu_stack | GroupVolAbnormalAlarm | 79
bamu_stack | bamu_stack | ContactorBreakAbnormalAlarm | 80
bamu_stack | bamu_stack | ContactorCloseAbnormalAlarm | 81
bamu_stack | bamu_stack | ChargeStopAlarm | 82
bamu_stack | bamu_stack | DischargeStopAlarm | 83
bamu_stack | bamu_stack | GroupOverTempAlarm1 | 84
bamu_stack | bamu_stack | GroupOverTempAlarm2 | 85
bamu_stack | bamu_stack | GroupOverTempAlarm3 | 86
bamu_stack | bamu_stack | ModuleOverVolAlarm1 | 87
bamu_stack | bamu_stack | ModuleOverVolAlarm2 | 88
bamu_stack | bamu_stack | ModuleOverVolAlarm3 | 89
bamu_stack | bamu_stack | ModuleUnderVolAlarm1 | 90
bamu_stack | bamu_stack | ModuleUnderVolAlarm2 | 91
bamu_stack | bamu_stack | ModuleUnderVolAlarm3 | 92
bamu_stack | bamu_stack | VolCollectDisconnectAlarm | 93
bamu_stack | bamu_stack | CurrCollectDisconnectAlarm | 94
bamu_stack | bamu_stack | Fault | 95
dido | dido | ChiFa_Switch_DI | 1
dido | dido | PV_Switch_DI | 2
dido | dido | Load_Switch_DI | 3
dido | dido | ChiFa_Singn_DI | 8
dido | dido | YellowLight | 9
dido | dido | GreenLight | 10
dido | dido | RedLight | 11
dido | dido | ChiFa_Switch_DO | 12
dido | dido | QacSplit | 13
pcs_smarten | pcs_smarten | Online | 0
pcs_smarten | pcs_smarten | Status | 1
pcs_smarten | pcs_smarten | OnGrid | 2
pcs_smarten | pcs_smarten | APhaseVoltage | 3
pcs_smarten | pcs_smarten | BPhaseVoltage | 4
pcs_smarten | pcs_smarten | CPhaseVoltage | 5
pcs_smarten | pcs_smarten | APhaseCurrent | 6
pcs_smarten | pcs_smarten | BPhaseCurrent | 7
pcs_smarten | pcs_smarten | CPhaseCurrent | 8
pcs_smarten | pcs_smarten | APhasePower | 9
pcs_smarten | pcs_smarten | BPhasePower | 10
pcs_smarten | pcs_smarten | CPhasePower | 11
pcs_smarten | pcs_smarten | APhaseApparentPower | 12
pcs_smarten | pcs_smarten | BPhaseApparentPower | 13
pcs_smarten | pcs_smarten | CPhaseApparentPower | 14
pcs_smarten | pcs_smarten | APhaseReactivePower | 15
pcs_smarten | pcs_smarten | BPhaseReactivePower | 16
pcs_smarten | pcs_smarten | CPhaseReactivePower | 17
pcs_smarten | pcs_smarten | APhasePowerFactor | 18
pcs_smarten | pcs_smarten | BPhasePowerFactor | 19
pcs_smarten | pcs_smarten | CPhasePowerFactor | 20
pcs_smarten | pcs_smarten | ACActivePower | 21
pcs_smarten | pcs_smarten | ACApparentPower | 22
pcs_smarten | pcs_smarten | ACReactivePower | 23
pcs_smarten | pcs_smarten | ACPowerFactor | 24
pcs_smarten | pcs_smarten | ACFrequency | 25
pcs_smarten | pcs_smarten | ModuleTemperature | 26
pcs_smarten | pcs_smarten | AmbientTemperature | 27
pcs_smarten | pcs_smarten | CabinetTemperature | 28
pcs_smarten | pcs_smarten | DCPower | 29
pcs_smarten | pcs_smarten | DCCurrent | 30
pcs_smarten | pcs_smarten | DCInputVoltage | 31
pcs_smarten | pcs_smarten | DCDischargeEnergy | 32
pcs_smarten | pcs_smarten | DCChargeEnergy | 33
pcs_smarten | pcs_smarten | GridABLineVoltage | 34
pcs_smarten | pcs_smarten | GridBCLineVoltage | 35
pcs_smarten | pcs_smarten | GridCALineVoltage | 36
pcs_smarten | pcs_smarten | GridAPhaseCurrent | 37
pcs_smarten | pcs_smarten | GridBPhaseCurrent | 38
pcs_smarten | pcs_smarten | GridCPhaseCurrent | 39
pcs_smarten | pcs_smarten | GridAPhasePower | 40
pcs_smarten | pcs_smarten | GridBPhasePower | 41
pcs_smarten | pcs_smarten | GridCPhasePower | 42
pcs_smarten | pcs_smarten | GridAPhaseApparentPower | 43
pcs_smarten | pcs_smarten | GridBPhaseApparentPower | 44
pcs_smarten | pcs_smarten | GridCPhaseApparentPower | 45
pcs_smarten | pcs_smarten | GridAPhaseReactivePower | 46
pcs_smarten | pcs_smarten | GridBPhaseReactivePower | 47
pcs_smarten | pcs_smarten | GridCPhaseReactivePower | 48
pcs_smarten | pcs_smarten | GridAPhasePowerFactor | 49
pcs_smarten | pcs_smarten | GridBPhasePowerFactor | 50
pcs_smarten | pcs_smarten | GridCPhasePowerFactor | 51
pcs_smarten | pcs_smarten | GridTotalActivePower | 52
pcs_smarten | pcs_smarten | GridTotalReactivePower | 53
pcs_smarten | pcs_smarten | GridTotalApparentPower | 54
pcs_smarten | pcs_smarten | GridTotalPowerFactor | 55
pcs_smarten | pcs_smarten | GridFrequency | 56
pcs_smarten | pcs_smarten | LoadABLineVoltage | 57
pcs_smarten | pcs_smarten | LoadBCLineVoltage | 58
pcs_smarten | pcs_smarten | LoadCALineVoltage | 59
pcs_smarten | pcs_smarten | LoadAPhaseCurrent | 60
pcs_smarten | pcs_smarten | LoadBPhaseCurrent | 61
pcs_smarten | pcs_smarten | LoadCPhaseCurrent | 62
pcs_smarten | pcs_smarten | LoadAPhasePower | 63
pcs_smarten | pcs_smarten | LoadBPhasePower | 64
pcs_smarten | pcs_smarten | LoadCPhasePower | 65
pcs_smarten | pcs_smarten | LoadAPhaseApparentPower | 66
pcs_smarten | pcs_smarten | LoadBPhaseApparentPower | 67
pcs_smarten | pcs_smarten | LoadCPhaseApparentPower | 68
pcs_smarten | pcs_smarten | LoadAPhaseReactivePower | 69
pcs_smarten | pcs_smarten | LoadBPhaseReactivePower | 70
pcs_smarten | pcs_smarten | LoadCPhaseReactivePower | 71
pcs_smarten | pcs_smarten | LoadAPhasePowerFactor | 72
pcs_smarten | pcs_smarten | LoadBPhasePowerFactor | 73
pcs_smarten | pcs_smarten | LoadCPhasePowerFactor | 74
pcs_smarten | pcs_smarten | LoadTotalActivePower | 75
pcs_smarten | pcs_smarten | LoadTotalApparentPower | 76
pcs_smarten | pcs_smarten | LoadTotalReactivePower | 77
pcs_smarten | pcs_smarten | LoadTotalPowerFactor | 78
pcs_smarten | pcs_smarten | LoadFrequency | 79
pcs_smarten | pcs_smarten | ACDischargeEnergy | 80
pcs_smarten | pcs_smarten | ACChargeEnergy | 81
pcs_smarten | pcs_smarten | DroopState | 82
pcs_smarten | pcs_smarten | SynchronizationState | 83
pcs_smarten | pcs_smarten | SynchronizationDoneState | 84
pcs_smarten | pcs_smarten | FaultState | 85
pcs_smarten | pcs_smarten | AlarmState | 86
pcs_smarten | pcs_smarten | TotalFanFault | 87
pcs_smarten | pcs_smarten | TotalAuxPowerFault | 88
pcs_smarten | pcs_smarten | TotalOverTemperatureFault | 89
pcs_smarten | pcs_smarten | TotalModuleOverCurrentFault | 90
pcs_smarten | pcs_smarten | TotalModuleCurrentLimitAlarm | 91
pcs_smarten | pcs_smarten | AmbientOverTemperatureFault | 92
pcs_smarten | pcs_smarten | ModuleCurrentUnbalanceFault | 93
pcs_smarten | pcs_smarten | EmergencyShutdown | 94
pcs_smarten | pcs_smarten | DspInitializingAbnormal | 95
pcs_smarten | pcs_smarten | DspVersionAbnormal | 96
pcs_smarten | pcs_smarten | DspParameterMismatch | 97
pcs_smarten | pcs_smarten | CpldVersionAbnormal | 98
pcs_smarten | pcs_smarten | FlashAbnormal | 99
pcs_smarten | pcs_smarten | MonitorInitializingAbnormal | 100
pcs_smarten | pcs_smarten | MonitorParameterMismatch | 101
pcs_smarten | pcs_smarten | HardwareVersionError | 102
pcs_smarten | pcs_smarten | IdReduplicatedFault | 103
pcs_smarten | pcs_smarten | CalibrationParameterError | 104
pcs_smarten | pcs_smarten | SamplingZeroPointError | 105
pcs_smarten | pcs_smarten | CanACommunicationFault | 106
pcs_smarten | pcs_smarten | CanBCommunicationFault | 107
pcs_smarten | pcs_smarten | CanCCommunicationFault | 108
pcs_smarten | pcs_smarten | CanDCommunicationFault | 109
pcs_smarten | pcs_smarten | Rs485_1CommunicationFault | 110
pcs_smarten | pcs_smarten | Rs485_2CommunicationFault | 111
pcs_smarten | pcs_smarten | Rs485_3CommunicationFault | 112
pcs_smarten | pcs_smarten | Rs485_4CommunicationFault | 113
pcs_smarten | pcs_smarten | AuxiliaryBoardCommunicationFault | 114
pcs_smarten | pcs_smarten | SpiCommunicationFault | 115
pcs_smarten | pcs_smarten | EmsCommConnectionTimeout | 116
pcs_smarten | pcs_smarten | Rs485CommunicationFault | 117
pcs_smarten | pcs_smarten | SynchronizationSignal1Fault | 118
pcs_smarten | pcs_smarten | SynchronizationSignal2Fault | 119
pcs_smarten | pcs_smarten | DcInputOvervoltage | 120
pcs_smarten | pcs_smarten | DcInputUndervoltage | 121
pcs_smarten | pcs_smarten | DcInputReverse | 122
pcs_smarten | pcs_smarten | DcOverloadAlarm | 123
pcs_smarten | pcs_smarten | DcOverloadTimeoutFault | 124
pcs_smarten | pcs_smarten | DcInputSoftStartFailure | 125
pcs_smarten | pcs_smarten | DcInputElectricControlSwitchOpenCircuit | 126
pcs_smarten | pcs_smarten | DcInputElectricControlSwitchShortCircuit | 127
pcs_smarten | pcs_smarten | DcInputGalvanicBreakDeviceHardwareFault | 128
pcs_smarten | pcs_smarten | DcInputSoftGalvanicBreakDeviceFault | 129
pcs_smarten | pcs_smarten | DcInputDryContactOpenCircuit | 130
pcs_smarten | pcs_smarten | DcBusOverVoltage | 131
pcs_smarten | pcs_smarten | DcBusUnderVoltage | 132
pcs_smarten | pcs_smarten | DcBusVoltageUnbalanced | 133
pcs_smarten | pcs_smarten | DcBusSoftStartFailed | 134
pcs_smarten | pcs_smarten | DcBusGalvanicBreakDeviceOpenCircuit | 135
pcs_smarten | pcs_smarten | DcBusGalvanicBreakDeviceShortCircuit | 136
pcs_smarten | pcs_smarten | DcBusGalvanicBreakDeviceHardwareFault | 137
pcs_smarten | pcs_smarten | DcBusSoftGalvanicBreakDeviceFault | 138
pcs_smarten | pcs_smarten | DcInsulationDetectAbnormal | 139
pcs_smarten | pcs_smarten | AcBusOverVoltage | 140
pcs_smarten | pcs_smarten | AcBusUnderVoltage | 141
pcs_smarten | pcs_smarten | AcBusOverFrequency | 142
pcs_smarten | pcs_smarten | AcBusUnderFrequency | 143
pcs_smarten | pcs_smarten | AcBusPhaseReversed | 144
pcs_smarten | pcs_smarten | AcBusVoltageUnbalance | 145
pcs_smarten | pcs_smarten | AcBusVoltageAbnormal | 146
pcs_smarten | pcs_smarten | AcBusPhaseLost | 147
pcs_smarten | pcs_smarten | IslandingProtection | 148
pcs_smarten | pcs_smarten | PllFailed | 149
pcs_smarten | pcs_smarten | AcCurrentDcComponentExcess | 150
pcs_smarten | pcs_smarten | AcOverloadAlarm | 151
pcs_smarten | pcs_smarten | AcOverloadTimeout | 152
pcs_smarten | pcs_smarten | AcBusConnectionForbidden | 153
pcs_smarten | pcs_smarten | AcBusNPhaseLoss | 154
pcs_smarten | pcs_smarten | AcSoftStartFailed | 155
pcs_smarten | pcs_smarten | AcGalvanicBreakDeviceOpenCircuit | 156
pcs_smarten | pcs_smarten | AcGalvanicBreakDeviceShortCircuit | 157
pcs_smarten | pcs_smarten | AcGalvanicBreakDeviceHardwareFault | 158
pcs_smarten | pcs_smarten | AcSoftStartGalvanicBreakDeviceFault | 159
pcs_smarten | pcs_smarten | GridOverVoltage | 160
pcs_smarten | pcs_smarten | GridUnderVoltage | 161
pcs_smarten | pcs_smarten | GridOverFrequency | 162
pcs_smarten | pcs_smarten | GridUnderFrequency | 163
pcs_smarten | pcs_smarten | GridPhaseReversed | 164
pcs_smarten | pcs_smarten | GridVoltageUnbalance | 165
pcs_smarten | pcs_smarten | GridVoltageAbnormal | 166
pcs_smarten | pcs_smarten | GridPhaseLoss | 167
pcs_smarten | pcs_smarten | GridNPhaseLoss | 168
pcs_smarten | pcs_smarten | GridPowerDown | 169
pcs_smarten | pcs_smarten | GridConnectionForbidden | 170
pcs_smarten | pcs_smarten | GridOverloadAlarm | 171
pcs_smarten | pcs_smarten | GridOverloadTimeoutFault | 172
pcs_smarten | pcs_smarten | AbnormalOffGridVoltage | 173
pcs_smarten | pcs_smarten | OffGridVoltageOscillation | 174
pcs_smarten | pcs_smarten | OffGridFrequencyAbnormal | 175
pcs_smarten | pcs_smarten | OffGridVoltagePhaseReversed | 176
pcs_smarten | pcs_smarten | OffGridVoltagePhaseLoss | 177
pcs_smarten | pcs_smarten | OffGridSoftStartFailure | 178
pcs_smarten | pcs_smarten | GridOffGridSwitchingError | 179
pcs_smarten | pcs_smarten | TotalDeratingAbnormal | 180
pcs_smarten | pcs_smarten | ModuleOvertempDerating | 181
pcs_smarten | pcs_smarten | CabinetOvertempDerating | 182
pcs_smarten | pcs_smarten | AmbientOvertempDerating | 183
pcs_smarten | pcs_smarten | BmsDryContactChargeForbidden | 184
pcs_smarten | pcs_smarten | BmsDryContactDischargeForbidden | 185
pcs_smarten | pcs_smarten | BmsShutdownFault | 186
pcs_smarten | pcs_smarten | BmsCommConnectionTimeout | 187
pcs_smarten | pcs_smarten | BmsDryContactFault | 188
sun_pv | sun_pv | Online | 0
sun_pv | sun_pv | MPPTStatus | 1
sun_pv | sun_pv | DailyGeneration | 2
sun_pv | sun_pv | MonthlyGeneration | 3
sun_pv | sun_pv | TotalGeneration | 4
sun_pv | sun_pv | RunningTime | 5
sun_pv | sun_pv | AmbientTemperature | 6
sun_pv | sun_pv | TotalActivePower | 7
sun_pv | sun_pv | TotalReactivePower | 8
sun_pv | sun_pv | TotalApparentPower | 9
sun_pv | sun_pv | DCTotalPower | 10
sun_pv | sun_pv | TotalPowerFactor | 11
sun_pv | sun_pv | Frequency | 12
sun_pv | sun_pv | APhaseVoltage | 13
sun_pv | sun_pv | BPhaseVoltage | 14
sun_pv | sun_pv | CPhaseVoltage | 15
sun_pv | sun_pv | APhaseCurrent | 16
sun_pv | sun_pv | BPhaseCurrent | 17
sun_pv | sun_pv | CPhaseCurrent | 18
sun_pv | sun_pv | Mppt1Voltage | 19
sun_pv | sun_pv | Mppt1Current | 20
sun_pv | sun_pv | Mppt2Voltage | 21
sun_pv | sun_pv | Mppt2Current | 22
sun_pv | sun_pv | Mppt3Voltage | 23
sun_pv | sun_pv | Mppt3Current | 24
sun_pv | sun_pv | Mppt4Voltage | 25
sun_pv | sun_pv | Mppt4Current | 26
sun_pv | sun_pv | Mppt5Voltage | 27
sun_pv | sun_pv | Mppt5Current | 28
sun_pv | sun_pv | Mppt6Voltage | 29
sun_pv | sun_pv | Mppt6Current | 30
sun_pv | sun_pv | Mppt7Voltage | 31
sun_pv | sun_pv | Mppt7Current | 32
sun_pv | sun_pv | Mppt8Voltage | 33
sun_pv | sun_pv | Mppt8Current | 34
sun_pv | sun_pv | Mppt9Voltage | 35
sun_pv | sun_pv | Mppt9Current | 36
sun_pv | sun_pv | Mppt10Voltage | 37
sun_pv | sun_pv | Mppt10Current | 38
sun_pv | sun_pv | Mppt11Voltage | 39
sun_pv | sun_pv | Mppt11Current | 40
sun_pv | sun_pv | Mppt12Voltage | 41
sun_pv | sun_pv | Mppt12Current | 42
sun_pv | sun_pv | GridOvervoltage | 43
sun_pv | sun_pv | GridUndervoltage | 44
sun_pv | sun_pv | GridOverfrequency | 45
sun_pv | sun_pv | GridUnderfrequency | 46
sun_pv | sun_pv | GridPowerOutage | 47
sun_pv | sun_pv | LeakageCurrentHigh | 48
sun_pv | sun_pv | GridAbnormality | 49
sun_pv | sun_pv | GridVoltageUnbalance | 50
sun_pv | sun_pv | PvBackupConnectionFault | 51
sun_pv | sun_pv | PvReverseConnectionAlarm | 52
sun_pv | sun_pv | PvAbnormalityAlarm | 53
sun_pv | sun_pv | MpptReverseConnection | 54
sun_pv | sun_pv | BoostCapOvervoltageAlarm | 55
sun_pv | sun_pv | BoostCapOvervoltageFault | 56
sun_pv | sun_pv | PvCableShortToGround | 57
sun_pv | sun_pv | StringCurrentBackflow | 58
sun_pv | sun_pv | PvGroundingFault | 59
sun_pv | sun_pv | SystemHardwareFault | 60
sun_pv | sun_pv | AmbientTempHigh | 61
sun_pv | sun_pv | AmbientTempLow | 62
sun_pv | sun_pv | InsulationResistanceLow | 63
sun_pv | sun_pv | GroundCableFault | 64
sun_pv | sun_pv | ArcFault | 65
sun_pv | sun_pv | MeterCtReverseAlarm | 66
sun_pv | sun_pv | MeterCommAbnormalityAlarm | 67
sun_pv | sun_pv | GridConflict | 68
sun_pv | sun_pv | InverterGridTiedCommAlarm | 69
sun_pv | sun_pv | SystemFault | 70
sun_pv | sun_pv | SystemAlarm | 71
sun_pv | sun_pv | PIDImpedanceAbnormal | 72
sun_pv | sun_pv | PIDFunctionAbnormal | 73
sun_pv | sun_pv | PIDVoltageCurrentProtection | 74

## 写库表路由
template | field_map | mysql | mysql_prefix
agc | agc |  | agc
amc_meter | amc_meter | load_meter
amc_meter | amc_meter | dg_meter
amc_meter | amc_meter | pv_meter
amc_meter | amc_meter | ess_meter
bamu_air | bamu_air |  | air
bamu_bms | bamu_bms |  | bms
bamu_stack | bamu_stack |  | bamu
dido | dido | dodi
pcs_smarten | pcs_smarten | pcs
sun_pv | sun_pv |  | sunpv